# Unseen Assessment — Instructor Answer Key & Grading Guide

Model answers for dnp3_assessment.pcap and mqtt_assessment.pcap. Frame numbers are exact (verified with tshark). Award points on the four-criterion rubric (below); enforce the two identification gates.

## Part A — dnp3_assessment.pcap (30 frames, 3 TCP streams)

A1 — actors.

| Source IP | DNP3 link addr | Role | Evidence |
| --- | --- | --- | --- |
| 10.30.0.5 | 100 | Primary master | Sends READ integrity/Class-0 polls (frames 4, 8) and a CONFIRM (frame 14) |
| 10.30.0.6 | 101 | Secondary read-only master | Sends only a READ Class-0 poll (frame 19); issues no controls or confirms |
| 10.30.0.66 | 10 | Neither — impersonates the outstation | Sends an UNSOLICITED RESPONSE (frame 26) claiming to be the outstation (link 10) |

The real outstation is 10.30.0.20 (link 10), which answers the polls (frames 6, 10, 21) and sends the one genuine unsolicited event (frame 12).

A2 — the malicious frame: frame 26, an UNSOLICITED RESPONSE (function 0x82). Tells (any three): 1. IP source 10.30.0.66 ≠ the real outstation’s 10.30.0.20, yet its DNP3 link source claims 10 (the outstation) — IP/link-owner mismatch. 2. It rides a separate TCP stream (to the master’s port) from the real outstation’s session. 3. Its reported breaker = open / 58.50 Hz contradicts the polls seconds earlier (frames 6/10, breaker closed / 60.00 Hz) and the parallel secondary-master read (frame 21). 4. It is a response (0x82), not a control — a “watch the SELECT/OPERATE” detection never fires on it. (Contrast: frame 12 is the genuine unsolicited — same link 10, but IP source 10.30.0.20, and consistent data.)

A3 — the lie vs. the truth. Frame 26 paints the breaker as OPEN (point 0 = 0, “tripped”) and frequency as 58.50 Hz (false under-frequency, value 5850). The true state from the legitimate polls: breaker CLOSED (binary input point 0 = 1 in frames 6/10/21) and frequency 60.00 Hz (analog = 6000). It is a loss-of-view / spoofed-reporting attack (MITRE ATT&CK for ICS T0856), inviting an unnecessary operator response.

A4 — why the proposed rule fails, and the fix. Two independent reasons: 1. The attack is an UNSOLICITED RESPONSE, not a control — the rule’s function-code filter (SELECT/OPERATE/…) never matches, so it is a guaranteed false-negative here. 2. It hard-codes a single master IP and ignores the legitimate secondary master 10.30.0.6, so it is simultaneously too narrow (misses spoofed responses) and, if broadened to “not a master,” would false-positive on 10.30.0.6. Rewrite: alarm when a given DNP3 link address appears from an unexpected source IP / TCP session (e.g., link 10 arriving from anything other than 10.30.0.20), and/or when an unsolicited response’s IP source ≠ the known outstation IP — with the legitimate master set {10.30.0.5, 10.30.0.6} allow-listed.

## Part B — mqtt_assessment.pcap (66 frames)

B1 — the harvest. Frames 47, 49, 51 (broker → 10.40.0.66), delivered immediately after the rogue’s SUBACK. The field proving they are stored, not live: the PUBLISH RETAIN flag = 1 (mqtt.retain==1) — live telemetry in this capture (e.g., frames 34, 55) has RETAIN = 0. Harvested topics and leaked values: - plant/line1/config → hi_setpoint 80, firmware 1.4.2, mode auto - plant/line1/command → the command schema and topic name ({"actuator":"pump1","cmd":"STOP"}) - plant/site/info → gateway edge-gw-3 and a service username svc_ingest

B2 — authN vs. authZ. Yes, the broker authenticated the rogue — the anonymous CONNECT is frame 39 (client mqtt-recon, no username/password) and the broker accepted it with CONNACK return code 0 in frame 41. So the harvest and the injection are authorization failures, not authentication: - The harvest is a missing read ACL — the setting that permitted the accept is allow_anonymous true; the setting that permitted the reads is the absence of a per-topic read ACL. - The injection (frame 57, PUBLISH to plant/line1/command) is a missing write ACL. - The flag that makes it persist is RETAIN = 1. Because it is retained, the broker stores it, replacing the legitimate “STOP”; when the pump controller next reconnects and subscribes plant/line1/command, the broker delivers the malicious retained “START / valve open” — so the pump starts on reconnect, long after the attacker has disconnected (frame 59).

B3 — why “reject #” fails, and the real fix. The #-block fails because: 1. The attacker already harvested the exact topic names (frames 47–51), so it can subscribe to each topic directly (plant/line1/command, …) without ever using #. 2. The injection is a PUBLISH, not a subscribe — blocking wildcard subscriptions does nothing to a write. The two controls that actually close it: (a) allow_anonymous false + authentication (client credentials or certs) so the rogue is refused at CONNECT before any topic access; and (b) per-topic read/write ACLs bound to identity, so even an authenticated client cannot read config/command/site or write to a command topic. (Defense in depth: disable retained messages on command topics, or require a retained-message purge policy.)

## Rubric (0–3 each, 12 total) and mastery gates

Score each of the four criteria — Identify · Interpret · Justify · Recommend-control — using the student worksheet’s rubric table. Mastery = ≥10/12, no criterion < 2, AND both gates: (A) student names frame 26, the spoofed UNSOLICITED RESPONSE, as the one malicious DNP3 frame; (B) student identifies the retained command PUBLISH (frame 57) as a persistent write-authorization abuse. Missing either gate → cap at Approaching. Bands: Mastery 10–12 (+gates) · Approaching 7–9 · Not yet ≤6.

Common partial-credit notes. Calling frame 12 (the genuine unsolicited) the attack is the classic Identify=0 error — both share link 10, but only frame 26 has the IP mismatch. Saying “MQTT has no authentication” is the classic Justify miss — the rogue was authenticated (frames 39/41); the failure is authorization. Proposing TLS as the harvest fix earns partial credit only: TLS stops an on-path sniffer but not an authenticated rogue reading via the broker — the gap here is ACLs, not encryption.